## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
8 | 5002040021468 | HF ANALYZER WITH ACCESSORIES FOR CEMS SYSTEM (ATTACHED TECHNICAL SPECIFICATION SHEET AND CONDITION) | Set | 1 | 1 | 1 | 1 | number
9 | 5002040021469 | HCL ANALYZER WITH ACCESSORIES FOR CEMS SYSTEM (ATTACHED TECHNICAL SPECIFICATION SHEET AND CONDITION) | Set | 1 | 1 | 1 | 1 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA | NA | NA
2 | QAP/ITP/QCP | NA | QP/E&I/QC/45 R00 | Approved
3 | Drawing(s) | NA | G.A.-22-61-© R00 ( For 22U Rack Enclosure ) | Internal Approved
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | AS Per PO Annexure & MOM | AS Per PO Annexure & MOM | NA
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
QAP Sr no 1: 100% Visual Check Inspection For No Damage, As per Po Annexure & Technical Specification Witenssed - Found As Per Requirement.
QAP Sr no 3: Terminations -Wirning termination of HCL & HF Gas Analyser check of input and output connection- Found As Per Requirement.
QAP Sr no 4: Communication check _ verifiy 4-20mA output accoding to reading - Found AS Per Requirement.
QAP Sr no 5:- Verification of HCL & HF Gas Analyzer performance;( HCL measuring range: 0- 60 Mg/Nm3 & & HF Measuring range: 0- 25 Mg/Nm3 ) & Bump Test Conducted With HCL gas - Found AS Per Requirement.

## Document reviewed
Document reviewed
Vendor Internal Inspection & Performance Certificate Like ( Mechanical Fittment, Visual Inspection, RTC Functioning, etc ) Reviewed - Found In Order
QAP Sr no 6:-Calibration test certificate of HCL & HF Gas Analyzer Reviewed - Found As per Requirement
Calibration Certificate of Measuring Instrument was Used For Inspection Reviewed - Found In Order

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Digital Vernier Caliper | 0 - 200mm | A1614327 | 28.12.2022 | .. |  | Yes | Yes
2 | Digital Multimeter | .. | 35000009 | 28.12.2022 | .. |  | Yes | No

## Areas of concerns
Areas Of Concern
Nil

## Pending Activities
Pending Activities from this visit
No

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: