## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2001023058 | Carbon Steel Cold Drawn Seamless Heat treated U tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2021. Size: 19.05 MM OD X 13 BWG [Minimum Thickness] X 5000 MM Leg Length. | number | 436 Nos. | 436 Nos. | 436 Nos. | 436 Nos. | number
2 | 2001533442 | Carbon Steel Cold Drawn Seamless Heat treated straight tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2021. Size: 19.05 MM OD X 2.11 MM Thk [Minimum Thickness] X 5000 MM Long. | number | 900 Nos. | 900 Nos. | 900 Nos. | 900 Nos. | meter
3 | 2001495994 | Carbon Steel Cold Drawn Seamless Heat treated straight tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2021. Size: 25.40 MM OD X 14 BWG [Minimum Thickness] X 6000 MM Long. | number | 410 Nos. | 410 Nos. | 410 Nos. | 410 Nos. | km
4 | 2000090945 | Carbon Steel Cold Drawn Seamless Heat treated straight tubes conforming to the Specification as per ASTM A179-90a [Reapproved 2012.] Size: 25.40 MM OD X 12 BWG [Minimum Thickness] X 6000 MM Long. | number | 2260 Nos. | 2260 Nos. | 2260 Nos. | 2260 Nos. | meter (number)
5 | 2001840171 | Carbon Steel Cold Drawn Seamless Heat treated straight tubes conforming to the Specification as per ASTM A210 Gr. A1. -02 Reapproved 2012. Size: 25.40 MM OD X 2.30 MM THK [Minimum Thickness] X 1000 MM Long. | number | 70 Nos. | 70 Nos. | 70 Nos. | 70 Nos. | km (number)
6 | 2001023058 | Carbon Steel Cold Drawn Seamless Heat treated U tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2021. Size: 19.05 MM OD X 13 BWG [Minimum Thickness] X 5000 MM Leg Length. | number | 436 Nos. | 436 Nos. | 436 Nos. | 436 Nos. | each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | RIL/MECH/QAP/10, Rev.00. Dated: 11.10.2019. | Not Applicable | Approved By RIL
3 | Drawing(s) | P.O. Sr. No. 01 & 6: GX-381.2/05HE-15-S3, Rev.1. | Not Applicable | Provided By RIL
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Reference documents :- 1. E&M-STATIC-PSIR-063, Rev.03. Dated: 31.10.2019. 2. RIL MOM points :- Email dated 04.01.2022. | Not Applicable | Provided By RIL Client Emai

## Stages Witnessed
Stages Witnessed
Sampling carried out for Chemical & Mechanical test as Tensile, Hardness, Flaring and Flattening as per approved QAP and relevant standard - found satisfactory
As per QAP stage no-. 2.3: Witnessed Mechanical tests (Tensile, Flattening, Flaring and Hardness Test) at manufacture in house testing Lab facilities - results found to meet the specification requirements
As per QAP stage no-2.4: Witnessed Eddy current test for 50 Nos. & 100% & 10% Qty on randomly selected from offer lot of straight tubes in random length as per ASTM E309 , RIL email ( For external artificial Transverse & longitudinal Notch ) , approved QAP Note-5 and acceptance standard SA 450 – No recordable Discontinuity observed, Hence found satisfactory.
QAP Note -5 :- Eddy current master test sample artificial notch dimension checked of tranverse & longitudinal notch as per approved QAP & ASTM E 309 - observed dimension found within tolerrance limits.
As per QAP stage no-2.5: Witnessed Ultrasonic test for 50 Nos. & 100% & 10% Qty on randomly selected from offer lot of straight tubes in random length as per ASTM E213 & acceptance standard SA 450 – No recordable indication observed. found satisfactory
As per QAP stage no-.2.9: Witnessed hydrostatic test at testing pressure 1200 PSI [G] & 1800 PSI [G] for 100% Qty of straight tubes in random length for each PO. Line items as per approved QAP- No Leakage / No Pressure drop observed during 30 seconds ( Min. ) holding time., hence test found satisfactory.
As per QAP stage no-.2.10: Visual inspection carried out at Internal & external surface as accessible area for surface finish on100% qty. of straight tubes in final length for each PO. Line items as per approved QAP – No injurious surface defects & Nor mechanical damages were observed, Hence Found satisfactory.
As per QAP stage no-. 2.11: Dimension checked on 10% random selected quantity of straight tubes in final length from offer lot for each PO. Line items as per approved QAP– observed dimension found within tolerance limits as per standard requirements
As per QAP stage no- 2.12: Verified Product Marking on straight tubes in final length for each PO. Line items as per approved QAP– found satisfactory
As per QAP stage no. : Witnessed Dye Penetrant test on 100% qty. of straight tubes in final length at both end of tubes for each PO. Line items (up to 150 mm length at outside diameter of tubes and at inside of tubes upto as accessible portion of length ) - No recordable indication observed, hence found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
As per QAP stage No. 1.1: Reviewed Photocopy of Raw material test certificates as declared by vendor as per approved QAP - Found to meet the specification requirements
As per QAP stage No. 2.1 : Reviewed Heat treatment (Annealing) chart / record as per approved QAP - Found in order.
As per QAP stage No- 2.2. : Reviewed Chemical analysis (Product analysis) test report as per approved QAP - mentioned chemical elements found to meet the relevant standard requirements.
As per QAP stage No. 2.14 : Reviewed protection & packing list as per approved QAP- Found in order.
Reviewed all inspection reports & calibration certificates of measuring instruments and pressure gauges - Found in order to have valid calibration for intended use.
As per QAP stage No. 2.13 : Reviewed of manufacture final test certificate [ EN 10204 Typ. 3.2] TC No. HMTIPL/QA/CS-0894/22, HMTIPL/QA/CS-0894A/22, HMTIPL/QA/CS-0894B/22 & HMTIPL/QA/CS-0894C/22 Dtd. 27.04.2022 - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Flat micrometer [OD] | 0-25mm | X-6568 | 01.12.2022 | CC100421000001111F. | Yes | No | Yes
2 | Flat micrometer [OD] | 25-50mm | X-5519 | 01.12.2022 | CC100421000001112F. | Yes | No | No
3 | Ball point micrometer [THK.] | 0-25mm | 66498515 | 01.12.2022 | CC100421000001115F. | Yes | No
4 | Measuring Tape | 0-15 Mtrs. | HMT-2/ A-19 | 01.12.2022 | CC100421000001116F. | Yes | No
5 | Pressure Gauge | 0-140 KG/CM2 (G) | B8099002 | 01.11.2022 | CC100421000001069/F. | Yes | No
6 | Pressure Gauge | 0-140 KG/CM2 (G) | B8099003 | 01.11.2022 | CC100421000001070/F. | Yes | No
7 | Pressure Gauge | 0-280 KG/CM2 (G) | L20110004 | 01.11.2022 | CC100421000001072/F. | Yes | No
8 | Pressure Gauge | 0-280 KG/CM2 (G) | L20110005 | 01.11.2022 | CC100421000001073/F. | Yes | No
9 | UTM M/c. | 600 KN | 244-18-19 | 10.10.2022 | KTS/N/133/21-22 | Yes | No
10 | Hardness Tester M/c. | 150 KGF | 07/07/043 | 21.04.2022 | RCC/04-2021/200101. | No | Yes
11 | Vernier Caliper | 0-300 mm | 10124562 | 21.04.2022 | RCC/04-2021/20023. | No | Yes

## Areas of concerns
Areas Of Concern
During inspection photography is strictly prohibited at M/s. Heavy Metal & Tubes [India] Private Limited, C.S. Plant.

## Pending Activities
Pending Activities from this visit
RIL P.O. Sr. No. 01 & 06 for U Tubes order, [As per approved QAP]

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: