## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | ….. | 123.502.046.200 BLOW DOWN VESSEL 26 LIT Drawing No-002.392.424.H28 | Piece | 2 | 2 | 2 | 2 | number
20 | ….. | 123.502.072.200 SEPARATOR STAGE 1 Drawing No-123502072200 | Piece | 2 | 2 | 2 | 2 | meter
30 | …. | 123.502.073.200 SEPARATOR STAGE 2 Drawing No-123502073200 | Piece | 2 | 2 | 2 | 2 | km
40 | …. | 123.502.074.200 SEPARATOR STAGE 3 Drawing No-123502074200 | Piece | 2 | 2 | 2 | 2 | meter (number)
50 | …. | 123.502.075.200 SEPARATOR STAGE 4 Drawing No-123502075200 | Piece | 2 | 2 | 2 | 2 | km (number)
70 | …. | 123.502.086.200 Condensate Drain Tank Drawing No-123502086200 | Piece | 1 | 1 | 1 | 1 | each
80 | …. | 123.502.088.200 Cooler Drawing No-123502088200 | Piece | 1 | 1 | 1 | 1 | Piece
90 | …. | 130.000.184.200 Condensate Header Drawing No-130000184200 | Piece | 1 | 1 | 1 | 1 | Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | AWS/BCG/ITP/01 Rev.0 | Approved by Client
3 | Drawing(s) | 002.392.424.H28 Rev-0 123502072200 Rev-0 123502073200 Rev-0 123502074200 Rev-0 123502075200 Rev-0 123502086200 Rev-0 123502088200 Rev-0 130.000.184.200 Rev-1 | Not Applicable | Client document.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
Hydro test 1. BLOW DOWN VESSEL 26 LIT Drawing No-002.392.424.H28 As per ITP Sr.no.-B3 Hydro test witnessed at 4.0 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 2. SEPARATOR STAGE 1 Drawing No-123502072200 As per ITP Sr.no.-B1 Hydro test witnessed 26 kg/cm2(g) for holding time 30 min.– no leakage or pressure drop observed during the holding period – Found acceptable. 3. SEPARATOR STAGE 2 Drawing No-123502073200 As per ITP Sr.no.-B1 Hydro test witnessed at 60 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 4. SEPARATOR STAGE 3 Drawing No-123502074200 As per ITP Sr.no.-B1 Hydro test witnessed at 160 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 5.SEPARATOR STAGE 4 Drawing No-123502075200 As per ITP Sr.no.-B1 Hydro test witnessed at 360 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 6. Condensate Drain Tank Drawing No-123502086200 As per ITP Sr.no.-B4 Hydro test witnessed at 8 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 7.Cooler Drawing No-123502088200 As per ITP Sr.no.-B5 Hydro test witnessed at 8 kg/cm2(g) for Gas tube side Stage 1 25 kg/cm2(g) for Gas tube side Stage 2 55 kg/cm2(g) for Gas tube sideStage 3 80 kg/cm2(g) for Gas tube sideStage 3 18 kg/cm2(g) forShell Side for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable. 8. Condensate Header Drawing No-130000184200 As per ITP Sr.no.-B6 Hydro test witnessed at 10 kg/cm2(g) for holding time 30 min. no leakage or pressure drop observed during the holding period – Found acceptable.
As per QAP clause B- Final dimensional inspection.-for above all items. 1. Dimensional inspection - Nozzle orientation, elevation, projection etc. checked as per drg. Found within acceptable limit. - Overall dimension inspection carried out as per drg. Found within acceptable limit.
As per QAP clause B- Final visual inspection.-for above all items. - Visual inspection carried out as found Satisfactory. - Weld visual inspection carried out found free of crack, undercut, porosity etc.
As per QAP clause B- LPT of weld joint.-for above all items. - LPT of weld joint witnessed as per ASME Sec. VIII Div.1. No any recordable indication observed. Found acceptable. - Weld visual inspection carried out found free of crack, undercut, porosity etc.

## Document reviewed
Document reviewed
Internal hydro test inspection reports are reviewed - Found acceptable.
Final dimensional inspection internal report reviewed - Found acceptable
Final visual inspection report reviewed - Found acceptable
As per QAP Sr no A- Material history chart reviewed as per drawing Found in order.MTC reviewed as per drawing and applicable specification. found in order.
Measuring Instruments calibration certificate reviewed. Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0-70 Kg/cm2 | AWS-70-08 | 28.07.2022 | UI/210728/2/009 Date-29.07.2021 | Yes |  | Yes
2 | Pressure Gauge | 0-210 Kg/cm2 | AWS-210-1 | 03.08.2022 | UI/210804/2/005 Date-04.08.2021 | Yes |  | No
3 | Pressure Gauge | 0-350 Kg/cm2 | AWS-350-05 | 28.07.2022 | UI/210728/2/007 Date-29.07.2021 | Yes
4 | Pressure Gauge | 0-700 Kg/cm2 | AWS-700-01 | 28.07.2022 | UI/210728/2/005 Date-29.07.2021 | Yes
5 | Pressure Gauge | 0-210 Kg/cm2 | AWS-210-6 | 28.07.2022 | UI/210728/2/013 Date-29.07.2021 | Yes
6 | Pressure Gauge | 0-42 Kg/cm2 | AWS-42-03 | 28.07.2022 | UI/210728/2/014 Date-29.07.2021 | Yes
7 | Pressure Gauge | 0-70 Kg/cm2 | AWS-70-07 | 28.07.2022 | UI/210728/2/008 Date-29.07.2021 | Yes
8 | Pressure Gauge | 0-100 Kg/cm2 | AWS-100-2 | 03.08.2022 | UI/210804/4/004 Date-04.08.2021 | Yes
9 | Pressure Gauge | 0-100 Kg/cm2 | AWS-100-2 | 28.07.2022 | UI/210728/2/015 Date-29.07.2021 | Yes
10 | Pressure Gauge | 0-10.6 Kg/cm2 | AWS-10.6-2 | 10.09.2022 | ULR-CC217621000017000F Date-11.09.2021 | Yes
11 | Pressure Gauge | 0-100 Kg/cm2 | AWS-100-2 | 10.09.2022 | ULR-CC217621000017002F Date-11.09.2021 | Yes
12 | Measurng Tape | 0-3M | AWS-MT-02 | 21.12.2021 | UI/201222/9-002 Date-22.12.2020 | Yes
13 | Vernier Caliper | 0-200mm | AWS-VC-200-1 | 27.07.2022 | UI/201728/2/16 28.07.2021 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: