## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
11 | P026600000537 | VESSEL ATMOSPHERIC, MOC:SS316L, FLASH TANK, FLT-02 PROJECT: MEE, NEW TAG NO. FLT 02 | number | 1 | 1 | 1 | 1 | number
12 | P026600000534 | VESSEL ATMOSPHERIC, MOC:SS316L, FLASH TANK, FLT-01 PROJECT: MEE, NEW TAG NO. FLT 01 | number | 1 | 1 | 1 | 1 | meter
15 | P026700001148 | VESSEL PRESSURE ,MOC:SS316L, CYCLONE SEPERATOR, CYS-04, PROJECT: MEE, NEW TAG NO. CYS 04 | number | 1 | 1 | 1 | 1 | km
17 | P007400000027 | DRYER ATFD, AGITATED THIN FILM DRYER, MOC: SS304, ATFD-02 PROJECT: MEE, NEW TAG NO. ATFD-02 | number | 1 | 1 | 1 | 1 | meter (number)
32 | P026700001150 | VESSEL PRESSURE, MOC:SS316L, CYCLONE SEPERATOR,CYS-02 PROJECT: MEE, NEW TAG NO. CYS 02 | number | 1 | 1 | 1 | 1 | km (number)
45 | P026600000532 | VESSEL ATMOSPHERIC, MOC:SS316L, PACKED COLUMN TANK, PCT 01 PROJECT: MEE, NEW TAG NO.PCT 01 | number | 1 | 1 | 1 | 1 | each
49 | P026600000533 | VESSEL ATMOSPHERIC, MOC:SS316L,PACKED COLUMN, PC-01 WITH SPRAY NOZZLE AND PALL RING PROJECT: MEE, NEW TAG NO. PC-01 | number | 1 | 1 | 1 | 1 | Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | SRF-SCB-PQ-QAP015-Vessel-Metallic; Rev. 05; Date: 01.01.2021 | Not Applicable | Approved with Commented by SRF
3 | Drawing(s) | Not Applicable | 1. PTS-120-23/CYS-02 (CYS-802) Rev. No. 2 2. PTS-120-23/CYS-04 (CYS-804) Rev. No. 2 3. PTS-120-23/FLT-02 (FLT-802) Rev. No. 2 4. PTS-120-23/FLT-01 (FLT-801) Rev. No. 2 5. PTS-120-23/ATFD-01, 02 (ATFD-801, 802) Rev. No. 1 6. PTS-120-23/PC-01 (PC-801) PCT-01 (PCT-801)Rev. No. 1 | Approved by SRF vide Email Dated 03.07.2023
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Area of Concerns Acceptance Email from SRF Ltd. | Not Applicable | Provided by SRF Ltd. on Date 04.07.2023 & --.--.2023

## Stages Witnessed
Stages Witnessed
ITP Sr. No.. 01: Plates, Nozzle Pipe, Nozzle Flanges, Gasket, Fasteners, Body Flange 1) Witnessed material identification of Pipes, Flanges and Plates as per approved Drawing, QAP & Material Identification Report Visual & Random Dimensions Check inspection for offered items, Found Satisfactory. 2) Verified Material / Product marking and co-related with Material Test Certificates Found Satisfactory. 3) Sampling carried out to Chemical, Mechanical for IS2062 Gr. E250 - Found satisfactory. 4) Sampling carried out to. IGC practice-E for SS / Duplex Plate, Pipe & Flanges and SS316L pipe Found satisfactory,
ITP Sr No. 1 - Witnessed Lab test for chemical, Mechanical for IS2062, IGC Pr. E with 250x Magnification for SS/Duplex material - Found meet the requirement.
QAP Sr. No. D.4 - Witnessed PMI test on Offered flanges of Weld overlay, PMI carried out on RF Diameter - Found satisfactory.
QAP Sr. No. E. 1.1: Internal & External Visual inspection carried out with respect to approved drawing, applicable codes - Found satisfactory.
QAP Sr. No. E. 1.1: Witnessed final dimension check with respect to approved drawing, applicable codes, Client's Email Dated 04.07.2023 - Found satisfactory.
QAP Sr. No. E. 1.2: Witnessed PMI check for all accesible SS/Alloy steel and Pressure part welding with respect to approved drawing, and procedure - Found satisfactory,
Tag No. CYS-802, CYS-804, FLT-802, FLT-801, PC-801, PCT-801 QAP Sr. No. E. 1.3: Witnessed Hydro Test of Complete Assembly of offered vessel (Horizontal Position) at applicable pressure and Holding time as per approved drawing and QAP ­ Neither any leakages nor pressure drop observed during Holding period - Found satisfactory.
Tag No. ATFD-802 QAP Sr. No. E. 1.5: Witnessed Jacket side Hydro Test of offered Tag No. ATFD­802 (Horizontal Position) at 12 Kg/cm2 actual test pressure with 01 Hour minimum holding period as per drawing provided by vendor and QAP ­ Neither any leakages nor pressure drop observed during Holding period.
QAP Sr. No. E. 1.7: Witnessed PMI check for lifting lug I Support plate accesible welding (CS to SS Joints) with respect to approved drawing, and procedure - Found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No. A.1 Pressure Part 1) Raw Material Reviewed Photo copy of Raw material test certificate for Plate, Pipe, Flange, Gasket, Fasteners, Body Flanges, for pressure part and same was verified with Original Colour copy. - Found to meet material specification.
QAP Sr. No. A.2 - Non Pressure Part 1) Raw Material Reviewed Photo copy of Raw material test certificate for Saddle, Structure, support plates, Davit arm, and baffle - Found to meet material specification.
QAP Sr. No. B. Dish Forming 1) Reviewed Dimensional & Visual Check inspection report. - Found in order. 2) Reviewed DPT test on Knuckle radius and Weld Edge - Found in order.
QAP Sr, No, D. Fabrication & Testing 1) Reviewed WPS, PQR, WPQ as per ASME Sec. IX - Found in order. 2)Reviewed Fit-up Inspection report for Shell Long Seam / Circ Seam Joints / Shell to Dish CS joints / Nozzle to Flanges Joint - Found in order. 3) Reviewed DPT after root run welding for Shell Long Seam / Circ Seam Joints / Shell to Dish CS joints / Nozzle to Flanges Joint -Found in order. 3) Reviewed Nozzle to Shell Joints - Fit-up, DPT after root run welding, Nozzle Inclination <0.5 deg, Nozzle Orientation / Projections - Found in order.
QAP Sr. No. D.4 -Reviewed Flanges RF Diameter and Depth after weld overlay report as per approved Drawing, Client's Email acceptance (waiver) Dated 01.06.2023 - Found in order. - Reviewed DPT test report on Flanges of Weld Overlay, DPT test on RF Diameter after weld Overlay, Client's Email acceptance (waiver) Dated 01.06.2023 - Found in order.
QAP Sr. No. E. Final Inspection 1) Name Plate Verification & Stamping. - Found in order. 2) Pneumatic Test of RF Pad & SO flanges with respect to approved drawing, applicable codes and NDT procedure. -Found in order. 3) Reviewed Material Heat Chart with MTC - Final in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern
none.

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
TKIS approval email Dated 18.11.2022 For Holding temperature for (621 to 648°C) for Tube to Tubesheet joints PWHT & TKIS approval email Dated 19.12.2022 For Name Plate Details
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: