## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
70 | 10031363 | LG 300 x W 300 x THK 42mm, MOCK UP BLOCK, SA182 Gr. F60 (UNS S32205) of ASME Sec. II Part-A (Ed.2019) + API 938 C (Ed.2015) | number | 1 | 1 | 1 | 1 | number
60 | 10031360 | TUBE SHEET Skt.No: SK-6228 Rev.2 (565ØxH42mm), SA182 Gr. F60 (UNS S32205) of ASME Sec. II Part-A (Ed.2019) + API 938 C (Ed.2015) | number | 1 | 1 | 1 | 1 | meter
130 | 10031362 | LG 300 x W 300 x THK 37mm, MOCK UP BLOCK, SA182 Gr. F60 (UNS S32205) of ASME Sec. II Part-A (Ed.2019) + API 938 C (Ed.2015) | number | 1 | 1 | 1 | 1 | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | TPS NO.: H-2565-2571_SA182 F60_FORG Rev.2 Dt.23-12-2021 | Not Applicable | Approved by ANUP
2 | QAP/ITP/QCP | Not Applicable | GLE/QAP/21-22/1405-03 DT. 26-10-2021 | Approved by ANUP
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 4 Identification of heat treated forging and Selection of test sample.
QAP Sr. No.5 Mechanical test (Tensile, hardness,Impact) at manufacturer's inhouse testing facility on samples identified by TUV – Found to meet applicable code and specification requirements. .
QAP Sr. No. 7 – UT witnessed @10% at proof machine condition as per SA388/SA388M of Article 23 of Sec. V (Ed.2019) & acceptance criteria as per PARA 3.3.4 of ASME Sec. VIII Div. 2 (Ed.2019) found satisfactory.
QAP Sr. No. 7 – DPT witnessed @10 % after final machining as per Article 6 of ASME SecV & acceptance criteria as per Appendix 8 of ASME Sec.VIII Div.1 (Ed.2019) found satisfactory.
QAP Sr. No. 8.1 Visual Inspection for surface finish checked on all items – No surface defect observed – found satisfactory.
QAP Sr.No 8.2 & 8.3 Dimension & Marking checked @10% randomly selected samples from each line item – found to meet the specification requirements.
QAP Sr.No 8.4 Hardness checked @10% randomly selected samples from each line item – found to meet the specification requirements.
QAP Sr.No 8.5 PMI checked @10% randomly selected samples from each line item – found to meet the specification requirements.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status,traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No. 1 Raw material test certificates photocopy reviewed for its technical content only as declared by manufacturer and endorsed by vendor– Found to meet the applicable code and project specification requirement.
QAP Sr. No. 3 Heat treatment chart reviewed & found in order.
QAP Sr. No. 5.1 IGC Test ASTM G48 Method B report reviewed & found in order.
QAP Sr. No. 5.2 Ferrite Test as per ASTM E 562 report reviewed & found in order.
QAP Sr. No.6 Product Chemical Analysis report reviewed & found in order.
QAP Sr. No.9 Material test certificates Number GLECO/J-1405/4661 Dt.Date 08.01.2022 & GLECO/J-1405/4943 Date 19.01.2022 reviewed and found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | VERNIER CALIPER | 0-300 MM | VC-29 | 26.12.2021 | NCL/F/2021/28/06 | Yes |  | Yes
2 | VERNIER CALIPER | 0-600 MM | VC-106 | 26.12.2021 | NCL/F/2021/28/10 | Yes |  | No
3 | VERNIER CALIPER | 0-1000 MM | VC-73 | 04.12.2021 | NCL/F/2021/04/11 | Yes
4 | Dynamic Hardness Machine | -- | 1181/14 | 16.07.2022 | RTA/2021/317/03 |  | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: