## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1.010/55 | FBC0127Z0-ADZZZZZZZZ | 0.5 in x 150 # x BLRF ASTM A 105 (Ed.2018) | number | 191 | 1 | 1 | 1 | number
1.110/158 | FBC0167V0-03AEZZZZZZ | 3.0"X0.75" x 600 # x Red. SWRF x SCH 160 ASTM A 105 (Ed.2018) | number | 3 | 3 | 3 | 3 | meter
1.150/33 | FBC0721Z0-AEZZZZZZZZ | 0.75 in x 150 # x BLFF (Galv) ASTM A 105 (Ed.2018) | number | 21 | 21 | 21 | 21 | km
1.260/51 | FSC0147Z0-AEZZAALZZZ | 0.75 in x 300 # x SWRF x SCH 160 ASTM A 105 (Ed.2018) | number | 122 | 1 | 1 | 1 | meter (number)
1.300/23 | FSC0167Z0-01ZZAASZZZ | 1.0 in x 600 # x SWRF x SCH XS ASTM A 105 (Ed.2018) | number | 3 | 3 | 3 | 3 | km (number)
1.780/65 | FGK0161Z0-02ZZZZZZZZ | 2.0 in x 600 # x FIG-8 FF ASTM A 105 (Ed.2018) | number | 4 | 4 | 4 | 4 | each
2.120/126 | FSC5147Z0-ADZZAALZZZ | 0.5 in x 300 # x SWRF x SCH 160 ASTM A 182 GR F5 (Ed.2019) | number | 2 | 2 | 2 | 2 | Piece
2.160/69 | FSC5167Z0-AEZZAALZZZ | 0.75 in x 600 # x SWRF x SCH 160 ASTM A 182 GR F5 (Ed.2019) | number | 7 | 1 | 1 | 1 | Test sample
2.180/127 | FSC5247Z0-ADZZAALZZZ | 0.5 in x 300 # x SWRF x SCH 160 ASTM A 182 GR F9 (Ed.2019) | number | 78 | 70 | 70 | 70 | AU - All Unit
2.200/106 | FSC5247Z0-AGZZAASZZZ | 1.5 in x 300 # x SWRF x SCH XS ASTM A 182 GR F9 (Ed.2019) | number | 71 | 69 | 69 | 69 | lot
2.280/3 | FWC5247Z0-02ZZAASZZZ | 2.0 in x 300 # x WNRF x SCH XS ASTM A 182 GR F9 (Ed.2019) | number | 96 | 96 | 96 | 96 | Set
2.300/26 | FWC5247Z0-10ZZAASZZZ | 10.0 in x 300 # x WNRF x SCH XS ASTM A 182 GR F9 (Ed.2019) | number | 5 | 5 | 5 | 5 | Running Meter
2.310/27 | FWC5247Z0-12ZZAASZZZ | 12.0 in x 300 # x WNRF x SCH XS ASTM A 182 GR F9 (Ed.2019) | number | 2 | 2 | 2 | 2 | kg
2.340/111 | FWC5277Z0-04ZZAAJZZZ | 4.0 in x 900 # x WNRF x SCH 120 ASTM A 182 GR F9 (Ed.2019) | number | 3 | 3 | 3 | 3 | metric ton (tonne)
2.380/146 | FWC5287Z0-ADZZAALZZZ | 0.5 in x 1500 # x WNRF x SCH 160 ASTM A 182 GR F9 (Ed.2019) | number | 7 | 7 | 7 | 7 | ton
2.390/119 | FWC5287Z0-AGZZAALZZZ | 1.5 in x 1500 # x WNRF x SCH 160 ASTM A 182 GR F9 (Ed.2019) | number | 8 | 8 | 8 | 8 | cubic millimetre
2.410/97 | FGK3741Z0-02ZZZZZZZZ | 2.0 in x 300 # x FIG-8 FF ASTM A 182 F11 CL2 (Ed.2019) | number | 2 | 2 | 2 | 2 | cubic centimeter
2.420/98 | FGK5221Z0-02ZZZZZZZZ | 2.0 in x 150 # x FIG-8 FF ASTM A 182 GR F9 (Ed.2019) | number | 1 | 1 | 1 | 1 | cubic meter
2.430/107 | FGK5241Z0-02ZZZZZZZZ | 2.0 in x 300 # x FIG-8 FF ASTM A 182 GR F9 (Ed.2019) | number | 2 | 2 | 2 | 2 | cubic inch
2.440/99 | FGK5271Z0-02ZZZZZZZZ | 2.0 in x 900 # x FIG-8 FF ASTM A 182 GR F9 (Ed.2019) | number | 2 | 2 | 2 | 2 | cubic foot
2.540/176 | FWC5267Z0-02ZZAASZZZ | 2.0 in x 600 # x WNRF x SCH XS ASTM A 182 GR F9 (Ed.2019) | number | 5 | 5 | 5 | 5 | mm
2.560/178 | FWC5289Z0-ADZZAALZZZ | 0.5 in x 1500 # x WNRTJ x SCH 160 ASTM A 182 GR F9 (Ed.2019) | number | 11 | 11 | 11 | 11 | cm
3.020/82 | FBC4347Z0-AEZZZZZZZZ | 0.75 in x 300 # x BLRF ASTM A 182 F304L (Ed.2019) | number | 9 | 4 | 4 | 4 | in
3.220/83 | FBC4627Z0-AEZZZZZZZZ | 0.75 in x 150 # x BLRF ASTM A 182 F316L (Ed.2019) | number | 1 | 1 | 1 | 1 | foot
3.240/86 | FGK4741Z0-02ZZZZZZZZ | 2.0 in x 300 # x FIG-8 FF ASTM A 182 F321 (Ed.2019) | number | 1 | 1 | 1 | 1 | mile
3.250/143 | FBC4127Z0-ADZZZZZZZZ | 0.5 in x 150 # x BLRF ASTM A 182 F304 (Ed.2019) | number | 12 | 12 | 12 | 12 | yard
1.910/182 | FGK5271Z1-02ZZZZZZZZ | 2.0 in x 900 # x FIG-8 FF x B 16.48 IBR ASTM A 182 GR F9 (Ed.2019) | number | 2 | 2 | 2 | 2 | liter
2.360/140 | FWC5277Z1-04ZZAAJZZZ | 4.0 in x 900 # x WNRF x SCH 120 x B 16.5 IBR ASTM A 182 GR F9 (Ed.2019) | number | 1 | 1 | 1 | 1 | kl
2.450/138 | FGK5271Z1-04ZZZZZZZZ | 4.0 in x 900 # x FIG-8 FF x B 16.48 IBR ASTM A 182 GR F9 (Ed.2019) | number | 1 | 1 | 1 | 1 | cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | B224-CDU-TPL-000-PP-MR-0018 Rev.1 B224-CDU-TPL-000-PP-SP-0010 Rev.1 | Not Applicable | Approved by Tata
2 | QAP/ITP/QCP | 6-81-0006 Rev.5 | Not Applicable | Approved by Tata
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | EIL Specs : 6-81-0001 Rev.3, 6-82-0003 Rev.2, 6-79-0013 Rev.1, 6-44-0053 Rev.6, 6-44-0082 Rev.A, 6-44-0083 Rev.A | Not Applicable | Approved by Tata

## Stages Witnessed
Stages Witnessed
ITP Sr. No. 3.3: Identification of heat treated forging and Selection of test sample for Chemical & Mechanical Testing.
ITP Sr. No. 3.5: Destructive Testing: Mechanical testing (Tensile & Hardness) at manufacturer's in-house testing facility on client representative samples – Found to meet applicable code and specification requirements.
ITP Sr. No. 3.5: IGC Test as per ASTM A262 Pr."E" for SS items at manufacturer's in-house testing facility on client representative samples – Found to meet applicable code and specification requirements.
ITP Sr. No. 3.5: Grain Size for "H" grade SS items at manufacturer's in-house testing facility on client representative samples – Found to meet applicable code and specification requirements.
ITP Sr. No. 4.1.1: Visual inspection (100 %) of offered lot of each line item - No surface imperfections were observed - found satisfactory.
ITP Sr. No. 4.1.2 & 4.1.4: Dimensional & marking inspection (10% - Min. 01 No.) of randomly selected samples from offered lot of each line item - Found to meet the code and standard requirements.
ITP Sr. No. 4.1.3: Hardness checked @10% of dimensional inspected items from each line item – found satisfactory.
ITP Sr. No. 4.2: PMI checked @10% of dimensional inspected items from each line item – found to meet the specification requirements.
ITP Sr. No. 4.3: Final Stamping: Inspected items @100% identified with TUV low stress stamp on OD near manufacturers marking (Double stamp on witnessed @10% and rest single)
GI coating checked @10% of dimensional inspected items – found to meet the specification requirements.

## Document reviewed
Document reviewed
ITP Sr. No. 2.1: Raw material test certificates photocopy reviewed for its technical content only as declared by manufacturer and endorsed by vendor– Found to meet the applicable code and project specification requirements.
ITP Sr. No. 3.2: Heat treatment chart reviewed and found in order.
ITP Sr. No. 3.4: Product chemical analysis lab test reports reviewed – Found to meet the applicable code and project specification requirements.
ITP Sr. No. 3.6: NDT: Surface & Internal imperfection – Liquid Penetrant Testing reports reviewed & found in order.
ITP Sr. No. 6.1: Manufacturer's Test Certificate No. GLECO/J-637/5402, GLECO/J-637/5403, GLECO/J-637/5404 Dated: 17.01.2023 reviewed and found in order.
IBR form IIIC number 8117454694/IBR/637-03 Date: 14.01.2023 reviewed & found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Annexure-A | _ | _ | Valid | _ |  |  | Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: