## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
30 | TSTLK1A4B1ZZ | DUPLEX STAINLESS STEEL SEAMLESS TUBES AS PER ASME SA789 UNS 31803 SIZE ­ 19.05MM OD X 2.77MM THK (AVG) X 13190MM L HEAT NO ­ 22L2508-1220 nos & 22L2580-1190 nos | meter | 83637.79 (6341 Nos.) | 16091.800 + 15696.100 (1220+1190=2410 Nos.) | 16091.800 + 15696.100 (1220+1190=2410 Nos.) | 16091.800 + 15696.100 (1220+1190=2410 Nos.) | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | 2022­23/03/00672/DOM REV­0 DTD­ 07.03.2023 | APPROVED WITH COMMENTS BY CLIENT DTD­ 16.03.2023
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | TDC NO ­ 2023­DV0613­TDC­T2 REV­0 | Not Applicable | PROVIDED BY CLIENT

## Stages Witnessed
Stages Witnessed
Sampling carried out for chemical test (product analysis), mechanical test (tensile, flaring, Hardness) , ferrite content, microstructure examination (Method­A), Corrosion test (Method­ C) ­ Found in order.
QAP CL­3 ­ Witnessed chemical analysis test (Product analysis) as per approved QAP ­ Found to meet material specification requirement.
QAP CL­4, 5 & 6 ­ Witnessed Mechanical testing (Tensile, Flaring & Hardness test) as per approved QAP on representative samples identified by TUV - Found to meet the specification requirements.
QAP CL­7 ­ Witnessed ferrite content test for offered qty as per approved QAP ­ Found within acceptable range.
QAP CL​-8 ​ Witnessed micro structure examination as per ASTM A923 method​A as per approved QAP ​ Found to meet material specification requirement.
QAP CL­9 ­ Witnessed corrosion test as per ASTM A923 method­C as per approved QAP ­ Found to meet material specification requirement.
QAP CL­10 ­ Witnessed eddy current test for randomly selected 10% qty from offered lot as per approved QAP ­ No recordable indication observed.
QAP CL­11 ­ Hydrostatic test Witnessed for 10% randomly selected Quantity at 1000 PSI(g) pressure as per approved QAP - No Leakage / No Pressure drop observed during 10 seconds holding time. Water used having chloride content less than 25 PPM.
QAP CL­12 ­ Visual inspection for surface finish carried out for 10% randomly selected tubes from offered as per approved QAP - no injurious surface defect observed on accessible area.
QAP CL­13 ­ Witnessed dimension measurement for randomly sleected 10% qty from offered lot as per approved QAP ­ Dimension found within tolerance limit.
QAP CL­14 ­ Witnessed thickness measurement by UT for randomly selected 5 % qty from offered lot as per approved QAP ­ Found acceptable.
QAP CL­15 ­ Witnessed OD ring gauge passing for randomly selected 10% qty from offered lot as per approved QAP ­ Found acceptable.
QAP CL­16 ­ Witnessed PMI for randomly selected 10% qty from offered lot as per approved QAP ­ Elements confirming specification grade requirement.
QAP Cl­17 ­ Witnessed DP test of randomly selected 10 % qty from offered lot at distance of 25mm from both ends as per approved QAP ­ No relevent indication observed.
QAP CL­18 ­ Randomly verified marking/stamping on tubes as per approved QAP ­ Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP CL­1 ­ Reviewed photocopy of raw material test certificate for offered qty as per approved QAP ­ Found to meet material specification requirement.
QAP CL­2 ­ Reviewed solution annealing heat treatment record for offered qty as per approved QAP ­ Found in order.
QAP CL­19 ­ Reviewed final test certificate no ­ MTCPL/2023­2024/1429-A, 1429-B DTD 30.10.2023 as per approved QAP ­ Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | OD Micrometer | 0-25 MM | MM-2 | 16.12.2023 | NCQC-M/171222/12 | Yes | No | Yes
2 | Thickness Micrometer | 0-25 MM | QMB-01 | 16.12.2023 | NCQC-M/171222/07 | Yes | No | No
3 | Hardness Tester | HRBW/HRC | 07/06/009 | 12.04.2024 | MTMS/NABL/04/2023/29687 | Yes | No
4 | Tensile Machine | 600 KN | 01/2023-6905 | 25.01.2024 | 230015/01 | Yes | No
5 | Vernier Caliper | 0-200 MM | VC-02 | 16.12.2023 | NCQC-M/171222/03 | Yes | No
6 | Measuring Tape | 0-15 Mtrs | M-MT-15 | 04.05.2024 | NCQC-M/050523/41 | Yes | No
7 | Pressure Gauge | 0-140 Kg/Cm2 | MP-03 | 06.12.2023 | NCQC-MO/070623/03 | Yes | No
8 | Ultrasonic Testing Machine | -- | SY650317 | 18.03.2024 | 320518011 DTD­ 19.03.2023 | No | Yes
9 | Eddy Current | 1 to 100 KHz | FTS-SPX-UX-41 | 11.12.2023 | CERT/FTS/232/2022-23 | No | Yes

## Areas of concerns
Areas Of Concern
Photography is prohibited at vendor place during inspection.

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: