## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 73063090 | Alloy steel seamless, Cold drawn seamless tubes as per SA-213 Gr. T22 of ASME Sec.II Part A Edition 2021. Tube Size: 50.80 mm OD X 5.50 mm Thickness (Min.) X 6000 mm Long. | number | 60 Nos. | 60 Nos. | 60 Nos. | 60 Nos. | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | RMTL/C-3931/22-23, Dated 10.05.2022. | Approved by Arrowcon. (QAP Approved by mail conformation)
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr.No.: Witnessed Sampling carried out for Chemical, Mechanical test (Tensile, Hardness, Flaring & Flattening test) – As per approved QAP & found acceptable.
QAP Sr. No: 4 to 7: Witnessed Mechanical Testing (Tensile Test, Flaring Test, Flattening Test & Hardness Test) as per approved QAP - found to meet the specification requirements.
QAP Sr. No: 8: Witnessed eddy current test for 10% randomly selected tubes carried out as per ASTM E-309 and acceptance as per SA1016 - No recordable discontinuity observed.
QAP Stage no.9: Hydrostatic test Witnessed 10% randomly selected quantity at 2500 psi [G] pressure, chloride content less than 10PPM as per approved QAP - No Leakage / No Pressure drop observed during 10 seconds holding time.
QAP Stage no.10: Witnessed PMI test 10% randomly selected tubes as per approved QAP - Found to meet the specification requirements.
QAP Sr. No: 11: Visual inspection carried out for 10% randomly selected tubes as per approved QAP -No any injuries surface/defect observed. Found Satisfactory.
QAP Sr. No: 11: Dimensional inspection and ring gauge passing carried out for 10% randomly selected tubes as per approved QAP -Dimensions found within tolerance limit.
QAP Sr. No: 12: Verified product marking on straight tubes for randomly quantity as per approved QAP - Found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No:1: Reviewed copy of Raw material test certificates declared by supplier - Found to meet the specification requirements.
QAP Sr. No:2: Reviewed Straight tubes normalizing & tempering record as per approved QAP - Found in order.
QAP Sr. No:3: Reviewed Chemical test report [Product Analysis] as per approved QAP - found to meet the specification requirements.
QAP Stage 13:- Reviewed Inspection test certificate type 3.2: RMTL/CS-167/22-23, Dated: 01.07.2022 – Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | ECT M/c | --- | FTS-EC-121-19 | 08.08.2022 | CERT/FTS/96C/2021-22 | No | Yes | Yes
2 | Micrometer OD | 50-75mm | S/N-17115247 | 03.08.2022 | CC100421000000700/F | Yes | No | No
3 | Micrometer THK | 0-25mm | S/N-06086600 | 03.08.2022 | CC100421000000688/F | Yes | No
4 | Measuring Tape | 0-15Mtr | M-Tape-A-01 | 04.01.2023 | CC100422000000011F | Yes | No
5 | Pressure Gauge | 0-420 KG/CM2 [G] | PG-37 | 04.07.2022 | CC100422000000022F | Yes | No
6 | Tensile M/c | 0-400 KN | 02/2005-3182 | 08.05.2023 | KTS/N/020/1-3/22-23 | Yes | No
7 | Hardness Tester | 150 KGF | 05/03/134 | 08.05.2023 | KTS/N/020/2-3/22-23 | Yes | No
8 | Vernier Caliper | 0-300 MM | S/N-18078646 | 04.01.2023 | CC100422000000009F | Yes | No
9 | PMI M/c | N.A. | 812523 | 27.03.2023 | Tii/CAL/RM/907 | No | Yes

## Areas of concerns
Areas Of Concern
During inspection photography is strictly prohibited at M/s. Ratnadeep Metal & Tubes Limited. Rajpur (C.S. Plant)

## Pending Activities
Pending Activities from this visit
None.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
10 % witnessed Straight tubes identified with hard single Stamped on tubes as “ "at near manufacturer marking.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: