## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2000273293 | CS, SEAMLESS, ELBOW 90° LR, BW, ASME B16.9, ASTM A234 GR. WPB-S, SIZE 3" X SCH STD, R=1.5D. | number | 50 | 50 | 50 | 50 | number
2 | 2000273293 | CS, SEAMLESS, ELBOW 90° LR, BW, ASME B16.9, ASTM A234 GR. WPB-S, SIZE 3" X SCH STD, R=1.5D. | number | 25 | 25 | 25 | 25 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | 10080-1-SS-PP-004 Part -II Rev.02 | Not Applicable | Issued by M/s RIL
2 | QAP/ITP/QCP | STOCK ITP/INSP/TOPAZ/01, Rev.3, dtd. 19/04/2021 (for CS Items) | Not Applicable | Approved by M/s RIL
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP Stage 9: Product hardness test witness 10% qty. for all offered items – Found within limit
ITP Stage 10: Penetrant test (10% Qty.) on Elbows at bevel ends – No recordable surface indication were observed.
ITP Stage 11: Visual inspection carried out on all fittings - No injurious surface defects were observed
ITP Stage 11: Dimensional inspection (10% - Min. 01 No.) randomly selected samples from offered lot of each line item - Found to meet the code and standard requirement.
ITP Stage 11.: Thickness checked by ultrasonic thickness gauge (10% Min.1 No.) on randomly selected sample from offered items for elbow outside and inside radious.- Found to meet dimensional standard requirements.
ITP Stage 12.: Marking & stamping verified - Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
ITP Stage 1: Pre-qualification type test record - Found to meet the code specification requirement.
ITP Stage 2: Raw material test certificates reviewed for its technical content only as declared by manufacturer and endorsed by Topaz Piping Industries- Found to meet the applicable code and project specification requirement.
ITP Stage 2.: Raw material identification ( carried out by Topaz TPIA)- Found to meet the applicable code & specification requirements
ITP Stage 4.: Forming report verified - Found in Order
ITP Stage 3 & 6.: Product sampling identification report ( carried out by Topaz TPIA) - Found satisfactory
ITP Stage 7.: Product chemical, Mechanical Lab test report witnessed by (witnessed by Topaz TPIA) for non IBR items - Found to meet the specification requirements
ITP Stage 9.: Hardness test reports - Found in order.
ITP Stage 10.: NDT test report - Found in order.
ITP Stage 13.: Manufacturer test certificates no.: 8129/2023-24, R.0 Dtd. 18.05.2023 - Found to meet the material specification requirements
Internal test/inspection reports, Calibration reports & pre-qualification type test report (earlier Qualified in witness of TPIA) of fittings - Found to meet the code specification requirement.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-5 Mtr | MT/3Mtrs/01 | 05.02.2024 | MH/CL/23/02/126/NABL, Dtd:06.02.2023 | Yes |  | Yes
2 | Digital Ultrasonic Thickness Gauge | 2 to 200 mm | 6924-9140 | 21.12.2023 | MH/CL/22/12/626/NABL, Dtd:22.12.2022 | Yes |  | No
3 | Portable Hardness Tester | --- | PHT-01 | 15.12.2023 | MH/CL/185W, Dated 17-12-2021 | Yes

## Areas of concerns
Areas Of Concern
REMARKS:-- Photographs are not allowed by Vendor during inspection. TPI hard stamp availability and verification on all fittings not possible just because of the Manufacturing process in carbin steel items.

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Inspected 100% stamped (Witnessed double & rest Single ) as “ ” near manufacturers marking
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: