## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
00010 | 8100002337 | 9003006312-0 GRAPHITE HEAT EXCHANGER CAPACITY- 15 M² P.R.No. 1200000376 TAG NO-3DHE-401A | number | 1.00 | 1.00 | 1.00 |  | number
00110 | 8100002338 | 9003006322-0 GRAPHITE HEAT EXCHANGER CAPACITY- 25 M² P.R.No. 1200000376 TAG NO-3DHE-331A | number | 1.00 | 1.00 | 1.00 |  | meter
00130 | 8100002338 | 9003006324-0 GRAPHITE HEAT EXCHANGER CAPACITY- 25 M² P.R.No. 1200000376 TAG NO-3DHE-332A | number | 1.00 | 1.00 | 1.00 |  | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | 1) 35/129/01 Rev - 00 dtd.28.03.2023 | Approved By Client ­ Anupam Rasayan
3 | Drawing(s) | Not Applicable | 1) 35/129/CR22"/12D/1P/4H REV-04 2) 35/129/CR18"/12D/3P/5H REV-04 | Approved in Code A by M/s Shroff & Associates Rep. Mr. V Chopra via mail Dtd. 21.03.2023.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per QAP Clause No C - (10).
A) Visual Inspection for Graphite Equipment outer surface & for internal surface upto accessible area carried out - Acceptable by client as per mail dtd 02.08.2023
As per QAP Clause No C - (10).
A) Dimensional Inspection of Graphite Equipment Witnessed. B) Dimensions for total length, height, Nozzle projections, Elevation, Nozzle size witnessed. C) Dimensions for Equipment Mouting / Foundation details (i.e C/C Distance, Hole Dia, Slot Size, base plate size etc) witnessed. - Found acceptable as drawing and per client mail Dtd. 02.08.2023
As per QAP Clause No C - (11).
A) Graphite Equipments Process side Hydro test witnessed at a pressure 5 kg/cm2 for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory. B) Graphite Equipments Service side Hydro test witnessed at a pressure 5.5 kg/cm2 for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification,calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
Instrument calibration certificate used for testing as provided by supplier reviewed ­ Found in order.
As per QAP Sr. No A1 : Graphite component internal test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A2 : End cover material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A3 : Service side nozzle material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A4 : Flanges material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A5 : Gasket material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A6 : Legs & support material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A7 : Helical spring & washer material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A8 : Earthing Boss material test certificate reviewed as provided by supplier - Found in order.
As per QAP Sr. No A9 : Tie rod & nut bolts material test certificate reviewed as provided by supplier - Found in order.
Inspection report of shell with rubber lined reviewed ­ Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0 - 5 Mtr | MT - 01 | 11.12.2023 | ME.2022/12/13/001 Dtd. 12.12.2022 | Yes |  | Yes
2 | Vernier Calliper | 0 - 300 mm | 403201172 | 2023-09-17 | ME.2022/09/51/001 Dtd. 18.09.2022 | Yes |  | No
3 | Pressure Guage | 0 - 10 kg/cm2 | J­22DMU­ D19­1562 | 17.12.2023 | 21­25325 Dtd. 18.01.2023 | Yes
4 | Pressure Guage | 0 - 10 kg/cm2 | J114DMU-L-21-702 | 31.12.2023 | 22-25452 Dtd. 02.01.2023 | Yes
5 | Pressure Guage | 0 - 10 kg/cm2 | J114DMU-L-21-719 | 31.12.2023 | 22-25453 Dtd. 02.01.2023 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: