## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 |  | V-6106 A/B,CAPACITY-6.52 KL,SS 316L FOR CAP-365 PROJECT | each | 2 | 2 | 2 | 2 | number
2 |  | Commissionning Spares for V-6106A/B FOR CAP-365 Project(200% Gasket for each flanged nozzle inclusing nozzle & 10% fasteners (Min,4 Nos.) for each size | each | 2 | 2 | 2 | 2 | meter
3 |  | V-6107,CAPACITY-6.52 KL,SS 316L FOR CAP PROJECT | each | 1 | 1 | 1 | 1 | km
4 |  | Commissionning Spares for V-6107 FOR CAP-365 Project(200% Gasket for each flanged nozzle inclusing nozzle & 10% fasteners (Min,4 Nos.) for each size | each | 1 | 1 | 1 | 1 | meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | QAP-PROJ-M_VESSEL-UPL Rev.R1 | Not Applicable | Issued by Client
3 | Drawing(s) | 1558-VFV-6106A REV.4 1558-VFV-6106B REV.4 1558-VFV-6107 REV.4 1558-VFSCT-6801 REV.3 | Not Applicable | Approved in Cose-A By Shroff & Associates (Engineers) Pvt. Ltd.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Clinet acceptance mail Dtd: 30.11.2021 for wave off of Paint DFT measurement on CS surfaces. And Client acceptance mail Dtd:27.11.2021 for acceptance of internal weld flus out not required and lifting lug & Man way orientation detail to be as built. | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Stage B.1,2 & 3: Raw material identification (for pressure parts) plates, pipes, flanges, fasteners & gaskets – Found to meet the approved drawing applicable code & project specification requirements
QAP Sr. No. C-1, Visual and Dimension of Dished end after forming (I.D, Ovality, inside circumference, profile using template, heights, straight face, over crowing measurement of true circular form on the inside of dished end on the straight face area using template & thinning) checked - found satisfactory as per the requirements mentioned in the drawing
QAP Sr. No. E1-1,E2-1, Random witness of longitudinal and circumferential seam set up inspection - found to meet the drawing requirements.
QAP Sr. No. E6-1, Nozzle marking on shell and Dish-Found to meet drawing requirement.
QAP Sr. No. F-1,Witnessed Final dimension of complete equipment after completion of all fabrication activities. Overall diamenrter,thickness,height,plimbness,roundness,bolt holes straddleness,lug dimension & orientation ,cladded flanges dimension & thickness,Nozzle dimensions,orientation,elevation,projection,inclination,inside supports and dip pipe length and antisphon hole drilling etc checked-Found within drawing requirement.
QAP Sr. No. F-1, Visual inspection of complete vessel inside and outside -No injurious surface defect was observed.
QAP Sr. No. E1-4,E2-4, Radiography films of all butt weld joint-Found no significant defect.
QAP Sr. No. F-2, PMI test of all SS surfaces,welds and overlays -Found to meet specificaiton requireement.
QAP Sr. No. F-3,Random witnessed Pneumatic test of Nozzle RF pads and SORF flanges and checked with soap solution- No leakage or presssure drop observed.
QAP Sr. No. F-4, Hydro test of complete equipment in horizontal condition at pressure 4.8 kg/cm2(g)[Required-4.55 kg/cm2 (g)] for holding time of 1 hour-No leakage or pressure drop observed during holding time.
QAP Sr. No.F7,Predispatch inspection carrried out and inside drying & cleanliness,Name plate varififcation ,Protection of open nozzle flanges,marking of degree& nozzle numbers on individual nozzles of equipment ,Painting on CS surfces & Pickling and passivation on SS surfaces and weld visually checked-Found as per drawing requirement.
QAP Sr.No.f7, Commissioning spares packing list physically verified-Found as per PO and drawing requirement.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. NoA2,F8-2 Copy of approved WPS/PQR/WPQ reviewed - Found to meet code and specification requirement.
QAP Sr.No.B1,2,3;F8-3- Raw material test certificates/traceability and check test reports of pressure parts as declared by manufacturer/lab and endorsed by M/s.Ishan – Found to meet the respective material specification, code and project specification requirement.
QAP Sr. No.B4; Weld consumable test cdertificate reviewed-Found as per code and specification requirement.
QAP Sr. No.E1,E2,E3,E6; Shell L-seam ,Shell C-seam ,Nozzle Pipe tp flange and Nozzle assembly to shell/Dish fit up reports-Found in order.
QAP Sr. No.E1,E2,E3,E6; DP test reports after backchip and root run of Shell L-seam ,Shell C-seam , Nozzle assembly to shell/Dish -Found in order.
QAP Sr. No.F8; Material heat chart and RT summary -Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | PRESSURE GAUGE | 0-10.4 KG/CM2 |  | 17.10.2022 | 20211018-10528-19 DT:18.10.2021 | Yes |  | Yes
2 | PRESSURE GAUGE | 0-10.4 KG/CM2 |  | 17.10.2022 | 20211018-10528-20 DT:18.10.2021 | Yes |  | No
3 | MEASURE TAPE | 0-5 METER | SE/MT/5MTRS/02 | 18.02.2022 | CCS/6826/20-21 DT:19.02.2021 | Yes
4 | MEASURE TAPE | 0-15 METER | SE/MT/15MTRS/02 | 18.02.2022 | CCS/6828/20-21 DT:19.02.2021 | Yes
5 | DIAL CALIPER | 0-300 MM | 5-5.14031255 | 19.10.2022 | 20211020-10528-9 DT:20.10.2021 | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
As per QAP

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: