## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
00170 | 2901902411 | HEAT EXCHANGER HEAT EXCHANGER FIXED TUBE SHEEL - TWO PASS EQUIPMENT : SECOND STAGE INTERCOOLER TYPE : BEU (H) SERVICE : SECOND STAGE INTERCOOLER TAG NO : 420-E-1002 A1/A2/B1/B2C1/C2 Gemini Job No. - 11540A to F | each | 6 | 6 | 6 | 6 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | B269-451-EE-PR-6040-0031 Rev. 00 |  | Issued by IOCL
2 | QAP/ITP/QCP |  | ITP-GEFL-IOCL-11351, Rev.00 | Approved by TUVI
3 | Drawing(s) |  | GEFL-IOCL-EIL-2149 Rev. 01 | Approved by EIL in code-R
4 | Procedure(s) | HARDNESS PROCEDURE- GEFL/P/021, HEAT TREATMENT PROCEDURE-GEFL/P/06, HYDRO-TEST PROCEDURE-GEFL/P/01, LPT PROCEDURE- GEFL/P/04, PMI PROCEDURE-GEFL/P/05, RT PROCEDURE-GEFL/P/005, PAINTING PROCEDURE- GEFL/P/023, GEFL/P/013
5 | Datasheet(s) | B269-420-80-42-DS-4002, Rev. 00 |  | Issued by IOCL
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
ITP Sr. No. 3.1 : Material identification of Plates, Pipes & Forgings material carried out by verifying dimension & Visual and correlating with MTCs for Pressure Parts – Found to meet the specification requirements.
ITP Sr. No. 3.3 : Indentification of cladding materail - Found to meet the Specification/drawing requirement.
ITP Sr. No. 5.1 : Visual & Dimensional Inspection carried out of Dished Ends for Main Shell & Channel shell - Found to meet the drawing requirement.
ITP Sr. No. 5.2 : Witnessed D. P. Test of Inside & Outside of Knuckle Portion & WEP of Dished Ends for Main Shell & Channel shell - No surface defect found.
ITP Sr. No. 6.1 : Witnessed Dimension of tubesheet after machining & drilling - Found to meet the drawing requirement.
ITP Sr. No. 7.4 : Reviewed radiography films for LS, CS & Nozzles joints of main shell assembly before PWHT- Found to meet the specification requirement.
ITP Sr. No. 7.5 : Witnessed final Dimensional of Main Shell assembly before PWHT - Found to meet the drawing requirement.
ITP Sr. No. 7.5 : Witnessed final weld visual of Main Shell assembly before PWHT - No surface defect found.
ITP Sr. No. 7.7 : Random Witnessed UT test of LS, CS & Nozzles joints of Main Shell assembly after PWHT - No recordable indication found.
ITP Sr. No. 7.8 : Random Witnessed Hardness test of LS, CS & Nozzles joints of Main Shell assembly after PWHT - Found to meet the specification requirement
ITP Sr. No. 8.3 : Reviewed radiography films for LS, CS & Nozzles joints of Channel shell before PWHT - Found to meet the specification requirement.
ITP Sr. No. 8.4 : Witnessed final Dimensional of Channel Shell assembly before PWHT - Found to meet the drawing requirement.
ITP Sr. No. 8.4 : Witnessed final weld visual of Channel Shell assembly before PWHT - No surface defect found.
ITP Sr. No. 8.6 : Random Witnessed Hardness test of LS, CS & Nozzles joints of Channel Shell assembly after PWHT - Found to meet the specification requirement
ITP Sr. No. 8.7 : Random Witnessed UT test of LS, CS & Nozzles joints of Channel Shell assembly after PWHT - No recordable indication found.
ITP Sr. No. 9.1 : Random witnessed sub-assembly of tube bundle before tubes insertion - Found to meet the drawing requirement
ITP Sr. No. 9.2 : Witnessed final alignment, completeness of tube bundle assembly after tubes insertion - Found to meet the drawing requirement
ITP Sr. No. 9.3 : Random witnessed pull through test of shell before tube bundle insertion - Found to meet the drawing requirement
ITP Sr. No. 9.4 & 9.5: Random witnessed of D.P test of root welding and witnessed D. P. test of final welding of tube to tube sheet joint - No surface defect found.
ITP Sr. No. 9.6 : Random witnessed of tube to tubesheet Expansion - Found to meet the drawing/specification requirement
ITP Sr. No. 10.1 : Witnessed PMI of all SS parts and it's welds - Found to meet the drawing/specification requirement
ITP Sr. No. 10.3 : Random witnessed DPT test & PMI of final weld overlay - Found to meet the drawing/specification requirement
ITP Sr. No. 10.5 : Witnessed Visual and Dimensional Inspection of complete assembly (In stack condition) - Found to meet the drawing requirement
ITP Sr. No. 10.6 : Witnessed Hydro test of shell side in stack condition at Pressure @ 126.1 kg/cm2 in horizontal condition at holding time of 60min duration - NO leakages or pressure drop found at time of Inspection.
ITP Sr. No. 10.7 : Witnessed Hydro test of tube side in stack condition at Pressure @ 97.1 kg/cm2 in horizontal condition at holding time of 60min duration - NO leakages or pressure drop found at time of Inspection.
ITP Sr. No. 10.8 : Random witnessed of final visual & DFT check of painting - Found to meet the specification requirement
ITP Sr. No. 10.11 : Random witnessed of Nitrogen filling at 0.5kg/cm2 pressure gauge and NRV valve - Found to meet the drawing/specification requirement

## Document reviewed
Document reviewed
ITP Sr. No. 2.1 : Inspection test plan - Found in order
ITP Sr. No. 2.2 : Procedure for Heat Treatment, Hardness, Hydrotest, NDT ( LT, UT, RT), WPS-PQR with Weld Plan,PMI procedure, Surface Preparation & Painting Procedure etc. - Found in order
ITP Sr. No. 3.2 : Material heat chart for non pressure parts - Found to meet the specification requirement
ITP Sr. No. 4 : WPS-PQR, WPQ & Mock Up of Tube to Tube sheet Joints - Found to meet the specification requirement
ITP Sr. No. 5.4 : PFHT graph for dished ends - Found to meet the specification requirement
ITP Sr. No. 6.2 : Buffles dimension report - Found to meet the drawing requirement
ITP Sr. No. 7.1 : Set up reports for Weld edge preparation & LS,CS,Pressure parts,etc - Found to meet the drawing requirement.
ITP Sr. No. 7.2 : Set up reports for Nozzle's to Main shell - Found to meet the drawing requirement.
ITP Sr. No. 7.6 : PWHT chart of Main shell assembly - Found to meet the drawing requirement
ITP Sr. No. 8.1 : Set up reports for Weld edge preparation & LS,CS,Nozzles & Pressure parts,etc - Found to meet the drawing requirement.
ITP Sr. No. 8.5 : PWHT chart of Channel shell assembly - Found to meet the drawing requirement
ITP Sr. No. 10.2 : Report for Clad/ weld overlay thickness check of all parts & Chips removal of weld overlays for Undilute chemistry - Found in order
ITP Sr. No. 10.4 : Pickling and Passivation report - Found in order
ITP Sr. No. 10.7 : Painting inspection report - Found to meet the drawing requirement
ITP Sr. No. 10.9 : Draining & Drying of Equipment inspection report - Found in order
ITP Sr. No. 10.10 : Name plate & Rub off details - Found in order
ITP Sr. No. 11 : Final documentation - Found in order
ITP Sr. No. 12 : Packing list - Found in order

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: