## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | NA | VLAVE DBBV_350 MM NB - ANSI 150 (MOV), VALVE SR NO.- 1055951,1055952, 1055953, 1055954, 1055955, 1055956 | number | 6 | 6 | REFER CONCLUSION |  | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA | NA | NA
2 | QAP/ITP/QCP | NA | GPIL-L04-P10-QA& QC-DI-A-105-R04 DT 29.10.2022 | By BPCL
3 | Drawing(s) | NA | GAD NO.- 946160000/02 | By BPCL
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | NA | NA | NA
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
1) ITP Clasue No. 4.10 - ITP Cl. Sr. No.- 4.10 - Witness Hydro static Test for shell as per the GPI Procedure for given pressure & duration & found no visual leakage, no pressure drops during the inspection hence Acceptable
2)  ITP Cl. Sr. No.-4.11 - Witness Hydro static Test for seat as per the GPI Procedurefor given pressure & duration & found no visual leakage, no pressure drops during the inspection hence Acceptable.
3) ITP Cl. Sr. No.-4.12 - Witness Hydro static Test additional seat test- DBB as per the GPI Procedure for given pressure & duration & found no visual leakage, no pressure drops during the inspection hence Acceptable. .
4) ITP Clasue No.- 4.14 100% Offered valve Low pressure air test witnessed at 80-100 PSI pressure & duration as per GAD & QAP, no leakage or pressure drop were observed test found satisfactory.
5) ITP Cl. Sr. No.- 4.14 - Witness torque test ( 1% of valve of all sizes/type) as per the GPI Procedure & results are found within acceptable limits as per procedure & approved GA drawing.
6) ITP Cl. Sr. No.- 4.15 - Witness DTR test as per the GPI Procedure & result found satisfactory
7) ITP Cl. Sr. No.- 4.16 - Witness drive train strength test ( 1% of valve of all sizes/type) as per the GPI Procedure no. GPIL-L03-P07-D&D-E014- R07-15072023 & found no any visual deformation of the drive train hence acceptable
5) ITP Clasue No.- 4.17- Witness (5% each size) for Offered valves for antistatic test as per GAD & QAP, test found satisfactory.
9) ITP Cl. Sr. No.- 4.18 - Witnessed visual & dimensional inspection for of offered valves randomly selected & results are found within limit as per approved GA Drawing.
10 ) ITP Clasue No.- 4.20 Witness fugitive emission test ( 1valve /size) as per QAP & standard and found satisfactory
11 ) ITP Clasue No.- 4.22 Witness cycle test ( 1valve /size) for 100 cycel as per QAP & standard and found satisfactory
12) ITP Clasue No.- 4.23 Witnessed strip down test (1 Valve each size/type) & found no any damages marks on Offred parts & again check hydro for shell & seat & found no any visual leakage during inspection hence acceptable.
13) ITP Cl. Sr. No.4.24- Witnessed functional/ operation of actuator operated DBB Valves by manual & actuator for Open & Close Operation. Found Smooth and Acceptable.

## Document reviewed
Document reviewed
1) ITP Cl. Sr. No.- 1.10, 1.11, 1.13, 1.14- Reviewed Body, Cap - Upper and Lower Supplier MTC, Visual Report as per EN 10204.3.1, & results are found within acceptable limits as per approved GA Drawing
2) ITP Cl. Sr. No.- 1.12, 1.15 & 1.16- Reviewed Body, Cap - Upper and Lower – Critical Dimension -Wall Thickness report, Hardness test report & Heat Treatment report & results are found acceptable.
3) ITP Cl. Sr. No.- 1.19- Reviewed Fasteners Supplier MTC as per EN 10204.3.1, Offered by vendor found in order, as per mentioned in Drawing.
4) ITP Cl. Sr. No.- 1.20 & 1.21 - Reviewed Slip Elastomer supplier MTC Report for physical properties as per EN 10204.3.1, Offered by vendor found in order.
5) ITP Cl. Sr. No.-2.13 – Reviewed coating ENP inspection report for Body and Plug found acceptable.
6) ITP Cl. Sr. No.- 3.14- Reviewed Body, Cap Upper and Lower - Surface NDE- MT Report, offered by vendor found in order.
7) ITP Cl. Sr. No.- 4.19 - Reviewed fire test report submitted by GPIL & found in order.
8) ITP Clasue No.- 4.25 Reviewed paint inspection report of offered valve as per GAD & found satisfactory
9) ITP Clasue No.- 4.26 & 4.27 Reviewed PDI report of offered valves for Name plate, Tag no & protection end covers as per QAP & found satisfactory
10) ITP Clasue No.- 4.28 Reviewed Spare list for as per submitted MR documents by M/s GPIL & found in order
11) ITP Clasue No.- 5.10 & 5.11 Reviewed COC EN 10204 3.1 & hydro test report offered valves as per ITP & standard & found in order
12 ) Review witness report of offered valves as per QAP & found satisfactory
13) Review sparelist of BPCL PR documents & found in order

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
| As attached | [6 empty] | Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit
NA

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Inspection found acceptable except mentioned in area of concern
IRN can be issued for PO Item numbers:
Expenses:
Remarks: