## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2002091924 | HOSE FLEXMET C/W CNN 1" 15 BAR 250MM Service: COOLING WATER Type: SS WIRE BRAIDED FLEXIBLE HOSE Construction: SS Mat: SS 304 Mat, lining: SS304 WIRE BRAID Connection welded-on: 1" FLANGE 150# Connection(s): 1" NPT(F) ON ONE END Mat, connections: SS304 Design spec, flange(s): A105 Pressure desig, flange: 15 KG/CM2 Thread: NPT Diameter, id mm 25.4(1 INCH) Design pressure: 15 KG/CM2 Length, overall m 250MM SS METALLIC BELLOW HOSE 1"X250 WITH 1" FLANGE #150 TAG.NO/Sr No/Func. Loc. : 1000274901 / VP00267/1140930/D / JDU-UTI-G723-MA-GUG723-F006 1000265545 / VP00267/1140930/C / JDU-UTI-G723-MA-GUG723-F005 1000255181 / VP00267/1140930/B / JDU-UTI-G723-MA-GUG723-F003 | each | 1 | 1 |  |  | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | QUALITY ASSURANCE PLAN- FINISHED PRODUCT, Rev. 0 Dtd.: 08.11.2021 | Approved by M/s. RIL via Mail Dtd.: 09.12.2021
3 | Drawing(s) | Not Applicable | JRE/RIL/01, Rev. 00, Dtd.: 02.11.2021 | Approved by M/s. RIL via Mail Dtd.: 09.12.2021
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 1: Visual witnessed on (10% or Min 01 no.) for hoses - No injurious defects observed.
QAP Sr. No. 1: Dimsnsional witnessed on (10% or Min 01 no.) for hoses - Found to meet drawing requirement.
QAP Sr. No. 4: Hydrotest witnessed on (10% or Min 01 no.) for hoses as per attached report at different pressures as mentioned in reports for a holding time of 5 min for each P.O. line item number - No leakage or pressure drop observed.
QAP Sr. No. 5: PMI witnessed on accesible area only for hoses - Found to meet requirements.
QAP Sr. No. 6: DP witnessed on Weld joint accesible area only for hoses - Found to meet requirements.
QAP Sr. No. 1: Marking & stamping witnessed for 100% - found in order.

## Document reviewed
Document reviewed
QAP Sr. No. 2: RMTC reviewed for Flanges Only as declared by manufacturer and endorsed by Vendor (JREPL) - Found to meet relevant specification.
QAP Sr. No. 3: Hose MTC report reviewed - Found to meet relevant specification.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0 - 42 Kg/cm2 | 42-5 | 27.01.2022 | PG-5220, Dtd.: 28.01.2021 | Yes |  | Yes
2 | Vernier Calliper | 0 - 300 mm | SC50704170042 | 22.10.2022 | D-587, Dtd.: 23.10.2021 | Yes |  | No
3 | PMI Machine | - | 814128 | 07.04.2022 | Tii/CAL/AE/723, Dtd.: 08.04.2021 | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: