## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
- |  | FULL THREADED STUD BOLT ASTM A193 GR.B7 WITH TWO HEAVY HEX NUT ASTM A194 GR.2H (S+2N) | [5 empty] | number
2 | 2000262390 | 0.500" UNC x 2.25" LG | each | 300 | 300 | 300 | 300 | meter
3 | 2000044195 | 0.500" UNC x 2.5" LG | each | 24 | 24 | 24 | 24 | km
4 | 2000044230 | 0.625" UNC x 4" LG | each | 232 | 232 | 232 | 232 | meter (number)
1 | 2000044474 | 1.250" UN8 x 8.75" LG | each | 70 | 70 | 70 | 70 | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not applicable | Not applicable | Not applicable
2 | QAP/ITP/QCP | RIL/MECH/QAP/01 Rev.0, DT: 16.07.2019 | Not applicable | Approved by RIL
3 | Drawing(s) | Not applicable | Not applicable | Not applicable
4 | Procedure(s) | Not Applicable | Not applicable | Not Applicable
5 | Datasheet(s) | Not applicable | Not applicable | Not applicable
6 | Others (Specify) | E&M­STATIC­PS/IR­017 REV.02 ISSUED .02 DT: 22.11.2019 | Not applicable | Issued by RIL

## Stages Witnessed
Stages Witnessed
QAP Sr. No.: 3.2 – Product Identification & sampling carried out for testing.
QAP Sr. No.: 3.2 – Product Tensile & Proof load test witnessed at NABL accredited lab on representative samples Identified by TUV – Found to meet the specification requirements.
QAP Sr. No.: 3.2 – Hardness test on randomly selected sample for each lot as per QAP at in house hardness testing facility of AEP – Found to meet the specification requirements.
QAP Sr. No.: 3.3 – Dimension check on 5% randomly selected samples from each line item – Found to meet the specification requirements.
QAP Sr. No.: 3.3 – Visual check on 5 % randomly selected samples from each line item – Found free of injurious defects.
QAP Sr. No.: 3.4 – Threads checked by std. GO / NO GO gauge on 5% randomly selected samples from each line item – Found satisfactory.
QAP Sr. No.: 3.5 – Marking & Stamping verified on randomly selected samples from each line item – Found to meet the specification requirements.
QAP Sr. No.: 3.6 – PMI test for studs as per QAP Note.4 – Found within specified limits of respective Material specification.
QAP Sr. No.: 3.8 – Rust preventive verified on randomly selected samples from each line item – Found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No.: 1.1 – Raw material test certificates reviewed for its technical content only as declared by manufacturer and endorsed by M/s AEPCOM – Found to meet the material specification requirements.
QAP Sr. No.: 2.2 – Heat treatment charts – Found to meet the specification requirements.
QAP Sr. No.: 3.1 – Product chemical lab test reports – Found to meet the specification requirements.
QAP Sr. No.: 3.10 – Manufacturer’s Test Certificate No.: AEPCOM/TC/332 Dtd.03.07.2023 – Found to meet the material specification requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern
Photography not allowed in M/s. AEPCOM premises - For client information

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
5% randomly selected & Inspected fasteners hard stamped on the face as " " & the remaining quantity identified with soft stamp as on the tags attached with gunny bags/boxes.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: