## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 10560-8451 | FULL THREADED STUD + HEAVY HEX NUT M39 X 2P X 210 MM LG. SA-479M TYPE 310S | number | 120 | 120 | 120 | 120 | number
2 | 10560-8452 | FULL THREADED STUD + HEAVY HEX NUT M16 X 2P X 195 MM LG. SA-479M TYPE 310S | number | 80 | 80 | 80 | 80 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | ARM No. R10560881 R.0 Dtd. 21.07.2022 | Not Applicable | Client Documents
2 | QAP/ITP/QCP | Annexure-1 to R10560881 : INSPECTION AND TEST PLAN FOR BOLTING MATERIAL | Not Applicable | Provided by L&T
3 | Drawing(s) | Not Applicable. | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Annexure-2 to R10560881 : STANDARD SPECIFICATION FOR PMI | Not Applicable | Provided by L&T

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 3.4 - Selection of sample for product testing ­ Found to meet applicable code and specification requirements.
QAP Sr. No. 3.5 & 3.6 - Product Chemical,Tensile, Proof Load, Hardness, Grain Size (as applicable) & IGC Pr "E" test at NABL accredited lab on representative sample identified by TUV - Found to ' meet applicable code and specification requirements.
QAP Sr. No. 4.1 - Visual inspection (2% Min 02 Nos.) from offered lot of each line item - Found free of injurious defects.
QAP Sr. No. 4.1 - Dimensional inspection (2% ­ Min. 02 Nos.) randomly selected samples from offered lot of each line item - Found to meet the code and standard requirement.
QAP Sr. No. 4.3 - PMI Test as per EIL spec (2% - Min 02 Nos.) randomly selected samples from offered lot of each line item – Found to meet the material specification requirements.
QAP sR. No. 4.1 & 4.2 - Marking & Stamping verified (2% - Min 02 Nos.) randomly selected samples from offered lot of each line item – Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP sR. No. 1.1 - NDT & Heat Treatment Procedure - Found to meet as per code & specification requirements.
QAP Sr. No. 2.1 - Raw material test certificate reviewed for its technical content only as declared by manufacturer and endorsed by (AEP) - Found to meet the applicable code and project specification requirement.
QAP Sr. No. 3.2 - Heat Treatment Chart/report ­ Found to meet the applicable code & specification requirement.
QAP Sr. No.4.3 - PMI test Reports ­ Found in order.
QAP Sr. No. 6.1 - Manufacturer test certificate No. AEPCOM/TC/1294 Dtd. 18.02.2023 ­ Found to meet the material specification requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Caliper | 0-300mm | T-10 | 22.10.2023 | 8445/N/2022 Dt.22.10.2022 | Yes |  | Yes
2 | Alloy Analyzer | - | 500N8274 | 08.06.2023 | Dtd. 07.06.2022 |  | Yes | No

## Areas of concerns
Areas Of Concern
Photography not allowed in M/s. AEPCOM premises - For Client information

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: