## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | 5005368 | Austenitic stainless steel welded straight tubes as per SA249 TP304 of ASME Sec. II, PartA, Edition2021, Size: 25.40mm OD X 1.20mm average thickness X 3000mm length, Heat No.:2208J0260- 8320 Nos. & Heat No.:220708A01- 6360 Nos. | number | 30000 | 14680 | 14680 | 14680 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | SS/WLD/01 Rev 00 Dated: 20.06.2021 and sampling plan as per client mail dated 09.09.2022 with inspection call. | Not Applicable | Approved by client with comment
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
Sampling has been done for chemical test (product analysis), mechanical tests (tensile test, flange test, flattening test, reverse bend test & hardness test) and IGC test practice "A" as per approved ITP & specification.
Witnessed mechanical tests (tensile test, flange test, flattening test, reverse bend test & hardness test) at manufacturer's inhouse testing facility- found to meet the specification requirement.
Witnessed Chemical test (Product analysis) & IGC test practice "A" as per ASTM A262 at NABL Lab as per sampling plan - found in order.
Witnessed hydro test for randomly selected tubes as per sampling plan in exact length at 1000psi(g) pressure- No leakage or no pressure drop observed During 2 Minute minimum holding time.
Visual inspection for surface finish carried out for randomly selected straight tubes as per sampling plan- no injurious surface defect observed.
Witnessed dimensional inspection for randomly selected straight tubes as per sampling plan- dimensions found within tolerance limit.
Marking verified on randomly selected straight tubes as per sampling plan- found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
Reviewed copy of raw material test certificates as provided by supplier- found in order.
Reviewed heat treatment records as per approved QAP- found in order.
Reviewed PMI Report - found in order.
Reviewed manufacturer's test certificate no.: MTCPL/2022-2023/1571-A & MTCPL/2022-2023-1571-B, Dated:11.01.2023 found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Digital Pressure gauge | 0-200 bar | 65092205 | 05.09.2023 | 030/22-23 Dated: 07/09/2022 | Yes | No | Yes
2 | Flat micrometer | 25-50mm | M-2 | 16.12.2023 | NCQC-M/171222/16 Dated.19.12.2022 | Yes | No | No
3 | Ball point micrometer | 0-25mm | QMB-01 | 16.12.2023 | NCQC-M/171222/07, Dated: 19.12.2022 | Yes | No
4 | Measuring tape | 0-15000mm | M-MT-15 | 05.05.2023 | NCQC-M/060522/26, Dated: 07.05.2021 | Yes | No
5 | UTM | 400KN | 010-07/08 | 21.04.2023 | MTMS/NABL/04/2022/27029, Dated: 24/04/2022 | Yes | No
6 | Hardness tester | -- | 07/06/009 | 20.04.2023 | MTMS/NABL/04/2022/27036, Dated: 21/04/2022 | Yes | No

## Areas of concerns
Areas Of Concern
Photography strictly prohibited at vendor place.

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: