## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2002010926 | Carbon Steel Cold Drawn Seamless Straight tubes conforming to the Specification as Per SA-179 of ASME SECTION ll, Part A, Edition 2021 , Size: 25.4mm OD X 2.11mm minimum thickness X 6020 mm length Heat No. 22F00682 | number | 1480 Nos. | 1480 Nos. | 1480 Nos. | 1480 Nos. | number
2 | 2002050304 | Carbon Steel Seamless Cold Drawn Heat treated U- tubes conforming to the Specification as Per SA-179 of ASME SECTION ll, Part A, Edition 2021 , Size: 20.0mm OD X 2.0 mm minimum thickness X 3000 mm leg length Heat No. 22F00682 | number | 134 Nos. | 134 Nos. | 134 Nos. | 134 Nos. | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | 1. QAP For U- tubes 2. QAP for CS HE Tubes to SA 179 ( For straight Tubes ) | Not Applicable | 1. Approved by RIL with comment , dated 31.01.2023 for U-Tubes 2. Approved by RIL , dated 09.02.2023 for Straight Tubes
3 | Drawing(s) | 1. U- tube drawing no. MI 2454 REV.03 2. Drawing for straight Tube :- 0030-MQ-UF-0101 Rev.03 | Not Applicable | Provided by RIL , Dtd. 09.02.2023
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Reference documents :- 1. RIL Email confirmation for drawing dtd. 09.02.2023 2. RIL Email confirmation for Mock- Up test dtd. 14.02.2023 3. REAM-STATIC-PSIR-063-REV-1 | Not Applicable | Client Email RIL specification

## Stages Witnessed
Stages Witnessed
Sampling carried out for straight tubes and U-tubes ( Per heat / Lot )as Chemical & Mechanical test as Tensile, Hardness, Flaring and Flattening as per approved ITP and relevant standard - found satisfactory
As per QAP stage no-. 2.3: Witnessed Straight tubes Mechanical tests as Tensile, Flattening, Flaring and Hardness Test for ( Per heat / Lot ) on TUV identified test samples with hard stamp and mechanical testing carried out at manufacture in house testing Lab facilities - results found to meet the specification requirements
As per QAP stage no-. 3.1: Witnessed U-tubes tubes Mechanical tests as Tensile, Flattening, Flaring and Hardness Test for ( Per heat / Lot ) on TUV identified test samples with hard stamp and mechanical testing carried out at manufacture in house testing Lab facilities - results found to meet the specification requirements
As per QAP stage No- 2.4. : Witnessed Chemical analysis (Product analysis) test for U- tubes at NABL laboratory as per approved QAP - mentioned chemical elements found to meet the relevant standard requirements.
As per QAP stage No- 2.2. : Witnessed ovality at U Bend portion on different location of U-tubes for each Rows on random selected 10% qty of U-Tubes as per approved QAP - Found within acceptable tolerance limits
As per QAP Clause No-2.3 - Witnessed DP Test on random selected 10% Qty of U-Tubes for U-Bend portion+300mm straight length eaither Leg ( for Inner most 06 rows ) as per approved QAP- No relevant indication observed , hence found satisfactory.
As per QAP Clause No. 2.5 : Witnessed U- Tubes Mock- up test ( Thining & ovality for inner most 03 row for 01 Nos. each ) per approved QAP - Found within acceptable limits as per TEMA Clause RCB 2.31.
As per QAP stage no-3.2 : Witnessed Eddy current test ( master sample for calibration having 0.8 mm Drill hole ) for [ P.O Line item- 01 ] on random selected 10% Quantity from offer lot of straight tubes in random length as per ASTM E309 and acceptance standard SA 450 – No recordable Discontinuity observed, Hence found satisfactory.
As per QAP stage no-3.4 : Witnessed Eddy current test ( master sample for calibration having transvers & longitudial notches as per approved QAP .) for [ P.O Line item- 02 ( U-tubes ) ] on random selected 50 Nos. Quantity from offer lot of straight tubes in random length as per ASTM E309 and acceptance standard SA 450 – No recordable Discontinuity observed, Hence found satisfactory.
As per QAP stage no-3.3: Witnessed Ultrasonic test ( master sample for calibration having OD & ID longitudinal notches) for [ P.O Sr. No. 01 straight tubes ]- 10% Quantity on randomly selected from offer lot of straight tubes condition in random length as per ASTM E213 & acceptance standard SA 450 – No recordable indication observed. found satisfactory
As per QAP stage no-3.4 : Witnessed Ultrasonic test ( master sample for calibration having OD & ID longitudinal notches ) for [ P.O Sr. No. 02- 50 Nos. Qty on randomly selected Quantity from offer lot in straight tubes condition in random length a as per ASTM E213 & acceptance standard SA 450 – No recordable indication observed. found satisfactory
As per QAP stage no-.4.1: Witnessed hydrostatic test at testing pressure 1500 Psi(g) for 100% Qty of straight Tubes in final length for PO. Line item-01 as per approved QAP- No Leakage / No Pressure drop observed during 10 seconds ( Min. ) holding time., hence test found satisfactory.
As per QAP stage no-.4.1 : Witnessed hydrostatic test at testing pressure 1000 Psi(g) for 100% Qty of U-Tubes ( For each radius ) for PO. Line item-02 as per approved QAP- No Leakage / No Pressure drop observed during 10 seconds ( Min. ) holding time., hence test found satisfactory.
As per QAP stage no-.4.2: Draining & drying checked of straight tubes & U-tubes ( For PO. Line item -1 & 2 ) in random selected 10% Quantity as per approved QAP :- found Free from water, moisture and foreign material .
As per QAP stage no-.3.1: Visual inspection carried out at Internal & external surface as accessible area for surface finish on random selected 20% qty. of straightTubes ( For PO. Line item-1 ) in final length as per approved QAP – No injurious surface defects & Nor mechanical damages were observed, Hence Found satisfactory.
As per QAP stage no-.3.3: Visual inspection carried out at Internal & external surface as accessible area for surface finish on random selected 10% qty. of U-Tubes ( For each radius ) as per approved QAP – No injurious surface defects & Nor mechanical damages were observed, Hence Found satisfactory.
As per QAP stage no-. 3.1 : Dimension checked on 20% random selected quantity of Straight Tubes ( For PO. Line item-1 ) in final length from offer lot for as per approved QAP– observed dimension found within tolerance limits as per standard requirements
As per QAP stage no-. 3.3 : Dimension checked on 10% random selected quantity of U-Tubes ( For each radius ) in final leg length as per approved QAP– observed dimension found within tolerance limits as per standard requirements
As per QAP stage no- 4.3: Verified Product Marking on straight tubes in final length in final length for PO. Line item-1 as per approved QAP– found satisfactory
As per QAP stage no- 4.3: Verified Product Marking on U-Tubes ( For each radius ) in final leg length for PO. Line item-2 as per approved QAP– found satisfactory
As per QAP stage no- 5 : Witnessed Preservation and Packing on 100 % quantity of U-Tubes and straight tubes for each PO. Line items as per approved QAP– found satisfactory
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
As per QAP stage No. 2.1: Reviewed Photocopy of Raw material test certificates as declared by vendor for ( PO. Line item -1 & 2 ) as per approved QAP - Found to meet the specification requirements
As per QAP stage No. 2.4 : Reviewed Heat treatment (Annealing) chart / record of ( PO. Line item -1 & 2 ) as per approved QAP - Found in order.
As per QAP stage No- 2.4. : Reviewed Chemical analysis (Product analysis) NABL test report for Straight tubes of ( PO. Line item - 1 ) as per approved QAP - mentioned chemical elements found to meet the relevant standard requirements.
As per QAP Clause No. 2.4 : Reviewed Stress relieving record /chart for U bend portion + 300 MM leg length of U- tubes after bending as per approved QAP & relevant standard - Found in order.
Reviewed calibration certificates of measuring instruments and pressure gauges - Found in order to have valid calibration for intended use.
As per QAP stage No. 4.4 : Reviewed of manufacture final test certificate ( EN 10204 Typ. 3.2 ) TC No. PAFL/TUBE/MTC/370 & PAFL/TUBE/MTC/371, Dtd. 17.02.2023 - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-15 Meter | MT-01 | 19.12.2023 | Paramount/78541 Dated :20.12.2022 | No | Yes | Yes
2 | Micrometer (OD) | 0-25 MM | MC-05 | 05.10.2023 | Paramount/75992 Dated :06.10.2022 | No | Yes | No
3 | Micrometer (OD) | 25-50 MM | MC-06 | 05.10.2023 | Paramount/75994 Dated :06.10.2022 | No | Yes
4 | Micrometer (THK.) | 0-25 MM | MC-04 | 05.10.2023 | Paramount/75993 Dated :06.10.2022 | No | Yes
5 | Rockwell Hardness Tester | Not Aplicable | 07/08/019 | 06.12.2023 | AKE/SRF/22/2504 Dated :- 08.12.2022 | Yes | No
6 | Pressure Gauge | 0 - 210 Kg/cm2 | PIPL-16103293 | 26.06.2023 | Paramount/78825 Dated :27.12.2022 | No | Yes
7 | Pressure Gauge | 0 - 210 Kg/cm2 | PIPL-16103295 | 26.06.2023 | Paramount/78827 Dated :27.12.2022 | No | Yes
8 | Vernier Calipper | 0-300 mm | V/C-01 | 21.05.2023 | Paramount/69819 Dated :22.05.2023 | No | Yes
9 | Eddy Current machine |  | Sr. No. FTS-SP-213/15 | 09.01.2024 | CERT/FTS/253/22-23 , Dated. 10.01.2023 | No | Yes
10 | UTM machine | 0-400 KN | 019/07-08 | 06.12.2023 | AHD/8121032262/UTM/100 , dated :- 07.12.2022 | Yes | No

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
100% witnessed U- tubes & straight tubes are identified with soft [Single] stamp as “ ”on paper tags fixed at each wooden box and inside of each wooden box for U-tubes and for straight tubes .
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: