## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2001824589 | Low Carbon Steel Cold Drawn Seamless Heat treated U tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2019. Size: 19.05 MM OD X 2.11 MM [Minimum Thickness] X 6500 MM Leg Length. [Radius No.1 to 18], Heat No.201886 | number | 777 Nos. | 777 Nos. | 777 Nos. | 777 Nos. | number
1 | 2001824589 | Low Carbon Steel Cold Drawn Seamless Heat treated Straight tubes conforming to the Specification as per SA-179 of ASME Section II Part A-Edition 2019. Size: 19.05 MM OD X 2.11 MM [Minimum Thickness] X 6356 MMLong, Heat No.201886 | number | 13 Nos. | 13 Nos. | 13 Nos. | 13 Nos. | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | RIL/Mech/QAP/10 Rev.02 Dated 27.12.2021 | Not Applicable | RIL Standard QAP
3 | Drawing(s) | 548-E-50 | Not Applicable | Drawings Provided by RIL.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Reference documents :- 1. E&M-STATIC-PSIR-063, Rev 04 Dated 27.12.2021 | Not Applicable | RIL Specification

## Stages Witnessed
Stages Witnessed
Sampling carried out for Chemical & Mechanical test as Tensile, Hardness, Flaring and Flattening as per approved ITP and relevant standard - found satisfactory.
QAP stage no-. 2.3: Witnessed Mechanical tests (Tensile, Flattening, Flaring and Hardness Test) on TUV identified test samples with hard stamp and mechanical testing carried out at manufacture in house testing Lab facilities - results found to meet the specification requirements
As per QAP stage no-2.4: Witnessed Eddy current test ( master sample for calibration having 0.8 mm Drill hole at 90 degree - 04 Nos.) on random selected 10% Quantity from offer lot of straight tubes in random length as per ASTM E309 and acceptance standard SA 450 – No recordable Discontinuity observed, Hence found satisfactory.
QAP stage No. 2.5: Witnessed Ultrasonic test for 10% and 50 Nos. randomly selected Quantity of straight tubes in random length as per ASTM E213 & acceptance standard SA 450 –Found Satisfactory.
QAP stage no. 2.9: Witnessed Hydrostatic Test at 1200 psi(g) pressure for 100% quantity for each PO items as per approved QAP- No Leakage / No Pressure drop observed during 30 seconds (Min.) holding time, hence test found satisfactory. Water used having chloride content less than 250 PPM.
QAP stage no .2.10: Visual inspection carried out at Internal & external surface as accessible area for surface finish on100% qty. of U tubes & Straight tube in final length for each PO. Line items as per approved QAP – No injurious surface defects & Nor mechanical damages were observed, Hence Found satisfactory.
QAP stage no. 2.11: Dimension checked on 10% random selected quantity of U tubes & Straight tube in final length from offer lot for each PO. Line items as per approved QAP– observed dimension found within tolerance limits as per standard requirements.
QAP stage no.2.12: Verified Product Marking on U tubes & Straight tube in final length for each PO. Line items as per approved QAP– found satisfactory.
QAP stage no.2.14: Verified Product packing on U tubes & Straight tube in final length for each PO. Line items as per approved QAP– found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
As per QAP stage No. 1.1: Reviewed Photocopy of Raw material test certificates as declared by vendor as per approved QAP - Found to meet the specification requirements
As per QAP stage No. 2.1 : Reviewed Heat treatment (Annealing) chart / record as per approved QAP - Found in order.
As per QAP stage No- 2.2. : Reviewed Chemical analysis (Product analysis) test report as per approved QAP - mentioned chemical elements found to meet the relevant standard requirements.
As per QAP Clause No. 2.6 : Reviewed U- Tubes Mock up test report ( Thining & ovality ) per approved QAP - Found in order as per TEMA Clause RCB 2.31
As per QAP Clause No. 2.7 : Reviewed Stress relieving record for U bend portion + 300 MM leg length of U- tubes as per approved QAP & relevant standard - Found in order.
As per QAP Clause No-2.8 - Reviewed DP Test report for U-Bend portion+300mm Leg. Length ( for Inner most 06 rows ) as per approved ITP- Found in order
As per QAP stage No. 2.13 : Reviewed of manufacture final test certificate ( EN 10204 Typ. 3.2 ) TC No. HMTIPL/QA/CS-1034A/22 , Dtd. 25.01.2023 - Found in order.
Reviewed calibration certificates of measuring instruments and pressure gauges - Found in order to have valid calibration for intended use.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Flat micrometer [OD] | 0-25mm | X-6576 | 21.04.2022 | RCC/04-2021/20029 , Dated. 23.04.2021 | No | Yes | Yes
2 | Ball point micrometer [THK.] | 0-25mm | 36033564 | 21.04.2022 | RCC/04-2021/20041 , Dated. 23.04.2021 | No | Yes | No
3 | Measuring Tape | 0-15 Mtrs. | HMT-2/ A-01 | 20.01.2022 | RICS/01-2021/19091 , Dated. 21.01.2021 | No | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
100% witnessed U- tubes & straight tubes are identified with soft [Single] stamp as “ ”on paper tags fixed at each wooden box and inside of each wooden box for U-tubes and for straight tubes .
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: